## Guidance Notes
Guidance Notes
1 | GM: 2021 In Operation aims to encourage buildings that have been previously certified before to continuously improve and maintain their performance.
2 | The assessment will be based solely on measured data. Letters of commitment or undertaking will not be accepted for GM2021 In Operation certification. All supporting documents—including the OSE report, IAQ audit, and POE survey—must be completed before the GM assessment begins.
3 | GM ratings may be adjusted based on actual building energy performance, only for SLE, ZE, and PE ratings. For instance, if a building previously certified with a GM GoldPLUS rating demonstrates performance that meets the GM2021 SLE requirements during assessment, it can be upgraded to GoldPLUS SLE status.
4 | How to calculate EUI for EE pathway1? Energy Use Intensity (EUI) measures a building's annual energy consumption. The calculation is: EUI = Total Annual Energy Consumption (kWh) ÷ Total Gross Floor Area (GFA) (m²) To determine your building's EUI: - Gather utility bills for the most recent 12-month period - Sum up the total energy consumption in kWh - Divide by your building's total gross floor area in m² Important: To qualify for the EUI pathway, your building must meet an occupancy rate above 60%.
5 | TSE (Total System Efficiency) is calculated differently based on your cooling system type: - For water-cooled or air-cooled chiller systems: TSE = Chiller plant efficiency + Air side (AHUs and/or FCUs) efficiency - For VRF or unitary systems: TSE = Condensing unit (CU) efficiency + Fan coil unit (FCU) efficiency (or AHU efficiency where applicable)
6 | DCS/DDC/CCS definition: The supply of chilled water for cooling purpose from a central source to multiple buildings through a network of pipes. Individual users purchase chilled water from the district cooling system operator and do not need to install their own chiller plant other than air distribution system. This is different from buildings’ in-house air-conditioning system, in part or in full, being maintained and operated by a third party.
7 | Under TSE requirement in GM2021 In Operation, is it required to measure TSE for all types of systems i.e. water cooled, air cooled and VRF system? Yes, it is necessary to measure Total System Efficiency. M&V for VRF systems is required if the VRF serving an aggregated aircon area greater than or equal to 2000m2 belongs to a single tenant or landlord and has undergone system replacement. However, permanent M&V is not required if the existing VRF is not replaced at the time of the GM assessment. For projects using VRF system and M&V is required, the CU efficiency can be based on catalogue and NEA formula until 31 Oct 2023 (LOA issued). From 1 Nov 2023, ongoing projects with VRF systems will need to measure their CUs' efficiency. For projects with VRF systems but M&V is not required, efficiency can be calculated based on equipment specifications. The OSE report should include water-cooled, air-cooled, VRF and air distribution system efficiency.
8 | For projects without permanent M&V for air side, how can the air side efficiency be measured? For projects without permanent M&V for airside, 3rd party energy audit for air side is required. Please see detailed requirement below: a) For AHUs with VSD (most projects), power readings should be downloaded from all AHUs to calculate air side efficiency; b) For AHUs without VSD (not common for GM certified projects), measurement must be taken with the sampling size of 30% for AHUs of each size (in terms of cooling capacity) with trend logging of power and cooling load for one week. The minimum number of AHUs to be measured is 5 and capped at max of 20 AHUs. When the actual number of AHUs on site is less than 5, all AHUs need to be measured. c) For FCUs, catalogue data can be used to do calculation This is valid till the next major retrofit when the building will be subject to GM2021 full certification.
9 | Does OSE report need to be endorsed by an Energy Auditor (EA)or PE(Mech) for GM2021 In Operation? Yes, endorsement is required for all independent OSE reports. However, if your building's on-site cooling system is linked to BCA's system, neither the OSE report nor its endorsement is needed.
11 | I have an existing building using chilled water system with one VRF at level one for a café, do I need to install M&V for this standalone VRF system? Permanent M&V is required only if when the VRF system and air distribution system serve an aggregate conditioned floor area of 2000m2 or more. Please refer to Code on Environmental Sustainability Measures for Existing Building (Edition 3) for permanent M&V requirements.

## 1. Project Details
GM: 2021 In Operation is applicable for Existing Buildings (a) which have previously attained Green Mark certification, (b) applying for re-certification and (c) have not done any major retrofit.
GM: 2021 In Operation
Project Details |  | Possible inputs
GM Reference No
Building name
Type of Building |  | Office / Retail / Hotel / Mixed Office + Retail
GFA (m2)
Carpark Area (m2)
Air-conditioned Area (m2)
Building Key Performance Data:
Type of Aircon system |  | Central Water-cooled Chiller Plant / VRF System / Unitary System
Building cooling load (RT)
Chiller configuration (e.g. 3 nos. x 500RT)
Cooling load / aircon area (W/m2) | #DIV/0!
Air-conditioning system efficiency (kW/RT) (Plant or CU)
Air Distribution system efficiency (kW/RT)
Total System Efficiency, TSE (kW/RT)
Total Building Energy consumption (kWh/yr)
Latest EUI (kWh/m2/yr)

## 2. EE requirement
Rating | Gold* | GoldPLUS | Platinum | SLE
% Energy efficiency improvement over 2005 levels* | 40% | 50% | 55% | 60%
Applicable EE Pathways: Pathway 1 – EUI; Pathway 2 – Fixed metrics
*Aligns with mandatory minimum energy efficiency requirements to raise energy performance standards of existing buildings

## 2.1 EE Pathway1
EUI Pathway1: for buildings with in-house Chilled water systems or other cooling systems |  |  |  |  | EUI Pathway1: for buildings supplied by DCS/DDC/CCS*
Building Type | Gold 40% | Goldplus 50% | Platinum 55% | SLE 60% | Building Type | Gold 40% | Goldplus 50% | Platinum 55% | SLE 60%
Commercial |  |  |  |  | Commercial
Office Buildings (Large) | 165 | 155 | 140 | 115 | Office Buildings (Large) | 120 | 100 | 90 | 80
Office Buildings (Small) | 150 | 135 | 120 | 100 | Office Buildings (Small) | 105 | 90 | 80 | 75
Hotels (Large) | 270 | 230 | 220 | 190 | Hotels (Large) | 180 | 149.5 | 134.55 | 119.6
Hotels (Small) | 200 | 180 | 160 | 140 | Hotels (Small) | 145 | 120.25 | 110 | 95
Retail Malls | 300 | 240 | 210 | 160 | Retail Malls | 190 | 160 | 144 | 128
Educational |  |  |  |  | Educational
IHL (University, Polytechnics and ITE) | 150 | 130 | 120 | 90 | IHL (University, Polytechnics and ITE)
Private Schools and Colleges | 130 | 110 | 100 | 80 | Private Schools and Colleges
Junior Colleges (MOE) | 70 | 60 | 50 | 40 | Junior Colleges (MOE) |  | nil
Secondary Schools (MOE) | 45 | 40 | 35 | 30 | Secondary Schools (MOE)
Primary Schools (MOE) | 45 | 40 | 35 | 30 | Primary Schools (MOE)
Healthcare |  |  |  |  | Healthcare
Hospitals (Private and General) | 450 | 375 | 340 | 300 | Hospitals (Private and General) | 295 | 245 | 230 | 210
Community Hospitals | 280 | 230 | 210 | 185 | Community Hospitals | 180 | 149.5 | 140 | 129.5
Polyclinic | 180 | 150 | 135 | 120 | Polyclinic | 120 | 100 | 90.45 | 85
Nursing/Youth Homes | 105 | 90 | 80 | 70 | Nursing/Youth Homes | 70 | 60 | 55 | 50
Other Non-Residential |  |  |  |  | Other Non-Residential
Mixed Develpments | by GFA mix |  |  |  | Mixed Develpments | by GFA mix
Community Centres | 180 | 150 | 125 | 110 | Community Centres | 120 | 100 | 90 | 80
Civic Buildings | 100 | 80 | 70 | 60 | Civic Buildings | 65 | 50 | 45 | 40
Cultural Institution | 220 | 180 | 140 | 120 | Cultural Institution | 140 | 115 | 100 | 85
Sports and Recreation Centres | 125 | 110 | 80 | 50 | Sports and Recreation Centres | 85 | 70 | 65 | 35
Religious/ Place of Worship | NA |  |  |  | Religious/ Place of Worship | NA
Industrial |  |  |  |  | Industrial
High Tech Industrial | NA |  |  |  | High Tech Industrial | NA
Light Industrial | 55 | 50 | 45 | 35 | Light Industrial
Warehouses, Workshops/Logistics and Others | 55 | 50 | 45 | 35 | Warehouses, Workshops/Logistics and Others
Residential |  |  |  |  | Residential
Non-Landed Residential (HDB, EC, Condo, pte apartments) | NA |  |  |  | Non-Landed Residential (HDB, EC, Condo, pte apartments) | NA
Cluster Housing |  |  |  |  | Cluster Housing
Landed Housing |  |  |  |  | Landed Housing
Additional Notes
Non Residential Buildings Minimum TSE |  | 0.9kW/RT
For ENRB using DCS/DDC/CCS*, air side minimum efficiency |  | 0.25kW/RT
On-site RE is included in EUI (net off) |  | On-site RE
EUI measured for EB and In Operation - occupancy rate |  | >60%
Excludes EV charging station consumption
EUI calculation:
Energy Utilisation Intensity =Total Building Energy Consumption of one year (kWhyr) / GFA (m2) Please use the most recent 12 months' energy consumption (occupancy rate >60%) to calculate the most recent EUI.
*DCS refers to the supply of chilled water for cooling purpose from a central source to multiple buildings through a network of pipes. Individual users purchase chilled water from the district cooling system operator and do not need to install their own air-conditioning plant. This is different from buildings’ in-house air-conditioning plant, in part or in full, being maintained and operated by a third party.

## 2.2 EE Pathway2
Building types | PARAMETER | Gold | GoldPLUS | Platinum | SLE
For Commercial buildings | ACMV TSE1 | 0.9 | 0.8 | 0.74 | 0.68
For Healthcare buildings |  | 0.9 | 0.8 | 0.75 | 0.7
For Educational buildings |  | 0.9 | 0.8 | 0.75 | 0.7
For High Tech/ High intensity Industrial buildings |  | 0.9 | 0.8 | 0.78 | 0.75
For Light industrial/ Warehouse buildings |  | 0.9 | 0.8 | 0.75 | 0.7
For other non Residential buildings |  | 0.9 | 0.8 | 0.75 | 0.7
For building supplied by DCS/DDC/CCS2
PARAMETER | Gold | GoldPLUS | Platinum | SLE
Air side efficiency | 0.25 | 0.2 | 0.18 | 0.16
Note: 1TSE is Total System Efficiency, including the efficiency from both chilled water plant and air side for water-cooled system; for VRF system, TSE includes the CU and FCUs efficiency 2DCS/DDC/CCS refers to the supply of chilled water for cooling purpose from a central source to multiple buildings through a network of pipes. Individual users purchase chilled water from the district cooling system operator and do not need to install their own air-conditioning plant. This is different from buildings’ in-house air-conditioning plant, in part or in full, being maintained and operated by a third party. 3For GM2021 full certification, M&V is required for TSE calculation/measurement; However, for project previously certified under legacy criteria, applying re-certification based on GM: 2021 In-Operation, air side efficiency can be done by third party energy audit. The methodology of air side measurement and its sampling size should refer to the guidance notes.
For Building with no air conditiong system, please use MV efficiency for compliance:
Efficiency (W/CMH)
Fan System | Gold | GoldPLUS | Platinum | SLE
Nameplate power | 0.35 | 0.32 | 0.28 | 0.25

## 3. OSE Report
Summary of OSE/Energy Audit Report (including airside efficiency) |  | Use "Insert..Object..Create from File" command if macro execution is disabled
Daily Average Reading | Period |  | Unit
| Day Time^ | Night Time~
Cooling Load |  |  | RT
Cooling Load Density (Air-con area) |  |  | m2/RT
Energy Consumption from Chilled water side (Chillers, Pumps, CTs) |  |  | kW
Chilled water supply temperature |  |  | oC
Chilled water return temperature |  |  | oC
Chilled water delta T |  |  | oC
Chilled water flow rate |  |  | l/s
Chilled water flow rate vs cooling load |  |  | USgpm/RT
*Condenser heat rejection |  |  | HRT
*Condenser water supply temperature |  |  | oC
*Condenser water return temperature |  |  | oC
*Condenser water delta T |  |  | oC
*Condenser water flow rate |  |  | l/s
*Condenser water flow rate vs cooling load |  |  | USgpm/RT
Chiller(s) efficiency |  |  | kW/RT
Chilled water pump(s) efficiency |  |  | kW/RT
*Condenser water pump(s) efficiency |  |  | kW/RT
*Cooling tower(s) efficiency |  |  | kW/RT
Overall chiller plant system efficiency |  |  | kW/RT
Energy consumption from airside |  |  | kW
Air Distribution system efficiency |  |  | kW/RT
Total System Efficiency (TSE) |  |  | kW/RT
*Not applicable to Air-cooled Chilled Water Plant
~For hotels and other developments with 24-hour operations only, night time shall refer to the period from 11pm-7am
^ For hotels and other developments with 24-hour operations, day-time shall refer to the period from 7am–11pm; for all other developments, daytime shall refer to the normal operating hours stipulated in clause 6.1.4
Summary of Heat Balance
| Data | Unit | Formula
Sum of total electrical energy used |  | kWh | (A)
Sum of total cooling produced |  | RTh | (B)
Sum of total heat rejected |  | RTh | (C)
Chiller Plant Efficiency |  | kW/RT | (A) / (B)
Total Heat Balance Data Count |  | - | (D)
Data Count > + 5% error |  | - | (E)
Data Count < - 5% error |  | - | (F)
Data Count within ±5% error |  | - | (G) = (D) – (E) – (F)
% Heat Balance within ±5% error |  | % | 100 x (G) / (D)
Click to Attach
Audit Report

## 4. Energy Consumption
Energy Use Intensity (3 Years Electricity Bill)
Energy Consumption (1st Year, Baseline)
Month | Total Consumption (kWh) | Tenant's Consumption (kWh) | Landlord's Consumption (kWh)
e.g. Jun'22 | 1228556 | 13401 | 1215155
Yearly Consumption | 1228556 | 13401 | 1215155
Energy Consumption (2nd Year)
Month | Total Consumption (kWh) | Tenant's Consumption (kWh) | Landlord's Consumption (kWh)
e.g. Jun'23 | 1096746 | 9944 | 1086802
Yearly Consumption | 1096746 | 9944 | 1086802
Baseline Improvement | 10.73%
Energy Consumption (3rd Year)
Month | Total Consumption (kWh) | Tenant's Consumption (kWh) | Landlord's Consumption (kWh)
e.g. Jun'24 | 1093303 | 11049 | 1082254
Yearly Consumption | 1093303 | 11049 | 1082254
Baseline Improvement | 11.01%
Computation of Energy Use Intensity (EUI) based on area (kW/m²/year)
| Year 1 | Year 2 | Year 3
Total Building Energy Consumption (kWh) | 1228556 | 1096746 | 1093303
Gross Floor Area,m² (GFA) | 45000
Energy Use Intensity, EUI | 27.3012 | 24.3721 | 24.2956
Deviation | Baseline | -10.73% | -11.01%
Reasons, if deviation > ± 5% | -

## 5. Water Consumption
Water Efficiency (3 Years Building Water Bill)
Water Consumption (1st Year, Baseline)
Month | Total Consumption (m³) | Tenant's Consumption (m³) | Landlord's Consumption (m³)
e.g. Jun'22 | 12256.1 | 376 | 11880.1
Yearly Consumption | 12256.1 | 376 | 11880.1
Water Consumption (2nd Year)
Month | Total Consumption (m³) | Tenant's Consumption (m³) | Landlord's Consumption (m³)
e.g. Jun'23 | 11682.2 | 603 | 11079.2
Yearly Consumption | 11682.2 | 603 | 11079.2
Baseline Improvement | 4.683%
Water Consumption (3rd Year)
Month | Total Consumption (m³) | Tenant's Consumption (m³) | Landlord's Consumption (m³)
e.g. Jun'24 | 10688.1 | 711 | 9977.1
Yearly Consumption | 10688.1 | 711 | 9977.1
Baseline Improvement | 12.79%
| Year 1 | Year 2 | Year 3
Total Building Water Consumption (m3) | 12256.1 | 11682.2 | 10688.1
Deviation | Baseline | -4.683% | -12.79%
Reasons, if deviation > ± 5% | -

## 6. Energy & Water Improve Plan
Energy and Water Improvement Plan
Submission of plans showing intent, measures and implementation strategies to achieve improvement target set against current performance over the next 3 years.
3 Years Energy Efficiency Improvement Target: | % | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
3 Years Water Efficiency Improvement Target: | % | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
Click to attach Energy Improvement Plan
Click to attach Water Improvement Plan

## 7. CoC
Cycles of Concentration (for water-cooled chiller plant only)
Submission of cooling tower’s water treatment reports showing 7 or better cycles of concentration.
Cycle of Concentration: | Cycles | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
Click to attach Water Treatment Report

## 8. Sustainable OM (hidden)
Sustainable Operations & Management
Occupant Satisfaction Survey
A post-occupancy evaluation is a survey to gauge occupants’ satisfaction on indoor environmental quality and identify corrective actions that will enhance comfort. Please ask your assessor for a survey weblink for this project, which may then be disseminated to occupants. Results will be tabulated automatically, so that FM may view them and record corrective actions taken. Alternatively, you may use the attached questionaire from Annex B of GM ENRB:2017, and tabulate the response with the attached result template. | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
Environmental Policy
Environmental Policy that reflects sustainability goals set for the building and its systems | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
Waste Recycling Reports
Name of waste recycling company: | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
Click to attach Occupant Satisfaction Result
Click to attach Environment Policy Statement
Clcik to attach Waste Recycling Reports
Click to attach scanned images of completed survey forms

## 8. IEQ
Indoor Environment Quality
IAQ Audit
Submission of latest IAQ audit report performed by SAC accredited consultants/companies, stating major areas of concern (e.g. mold issues).
Test Report Number: | Use "Insert..Object..Create from File" command if macro execution is disabled
Date Audit was Conducted:
Name of SAC-Accredited Lab:
Assessor's comment:
Lighting Lux Level
Submission of lighting lux levels for various areas, complying with SS531 or CP38.
Test Report Number: | Use "Insert..Object..Create from File" command if macro execution is disabled
Measurements taken by:
Assessor's comment:
Noise Level
Submission of noise levels for internal areas, complying with SS553 or CP13.
Test Report Number: | Use "Insert..Object..Create from File" command if macro execution is disabled
Measurements taken by:
Assessor's comment:
Click to attach IAQ Audit Report
Click to attach Lux Level Reading
Click to attach Noise Level Reading

## 9. Others
POE survey
Submit POE survey results | done within past one year
Waste reports
Submit past one year's waste collection report detailing the breakdown of types and quantity of recyclables and non-recyclables
Waste report of recyclables and non-recyclables
Tenants/Occupants engagement
Submit photos of health and wellbeing related activities | At least 3 activities per year
Click to attach waste reports of recycles and non-recycles
Click to attach photos of activities organised by Green Building Committee
Click to attach POE survey