## Instructions
To overcome the current limitation of the 360 capture, agencies would need the project team to attached photos to show compliance
Legend
Description of Requirement | Explanation of the agency's requirement
Acceptable Requirements | Range of acceptable measurements
Areas | Location on the plan
Specific Item | Specfic descripton of the item
Quantity | Number of sample attachment needed
Mode of Evidence | Type of documentation required (eg. video, photo, documents)
Description of Attachment | Infomation on what the attachment needs to show

## Requirements
For Project Team to Fill
S/n | Description of Requirement | Acceptable Requirements | Areas | Specific Item | Quantity | Mode of Evidence | Description of Attachment | Agency | Code/Regulation | Recorded in Platform (Yes, No, NA for the project) | Remarks | Photo Required for LiDAR capture
1 | The height of a barrier shall not be less than 1.0 m at all locations | >1000mm | All Applicable Areas | Barriers | 3 | Photo of Measurement |  | BCA | Approved Document
2 | The barrier shall not be less than 1000mm or 850mm when measured from the last climbable toehold whichever is higher | >850mm or >1000mm | All Applicable Areas | Barriers | 3 | Photo of Measurement |  | BCA | Approved Document
4 | In non-industrial buildings, the size of any opening or gap in a barrier shall not be larger than 100mm diameter sphere. | >150mm | All Applicable Areas | Barriers | 3 | Photo of Measurement |  | BCA | Approved Document
5 | In industrial buildings, the size of any opening or gap in a barrier shall not be larger than 150mm diameter sphere. | >150mm | All Applicable Areas | Barriers | 3 | Photo of Measurement |  | BCA | Approved Document
6 | Gratings and gaps along the accessible route <12mm | <12mm | All Applicable Areas | Common Areas Accessible Route | 1 | Photo of Measurement |  | BCA | Code of Accessibility |  |  | Yes
7 | Width min. 1500mm (Primary Accessible Route) | >1500mm | All Applicable Areas | Common Areas Accessible Route | 3 | Photo of Measurement |  | BCA | Code of Accessibility
8 | Width min. 1200mm (Secondary Accessible Route) | >1200mm | All Applicable Areas | Common Areas Accessible Route | 3 | Photo of Measurement |  | BCA | Code of Accessibility
9 | Operating Controls and Devices should be located at a height of between 450 mm to 1200 mm from the floor level | 1200mm > x > 450mm | All Applicable Areas | Common Areas Accessible Route | 1 | Photo of Measurement |  | BCA | Code of Accessibility
10 | The operating part of controls, electrical sockets and switches shall be located at 350 mm or more from the internal corner of a room or obstruction as shown in Figure 64 (c). | >350mm | All Applicable Areas | Common Areas Accessible Route | 1 | Photo of Measurement |  | BCA | Code of Accessibility
11 | Headroom > 2.0 m (Common circulation space) | >2000mm | All Applicable Areas | Common Areas Accessible Route | 3 | Photo of Measurement |  | BCA | Approved Document
13 | The doorway of the entrance must be 850mm minimum for a single leaf door. If the doorway has two independently operated door leaves, at least one active leaf must be a minimum of 850mm | >850mm | All Applicable Areas | Door | 1 | Photo of Measurement |  | BCA | Code of Accessibility
14 | On the pull side, a minimum space of 600 mm adjacent to the leading edge of the door with a minimum clear floor space of 1500 mm wide by 1500 mm deep | >600mm | All Applicable Areas | Door | 1 | Photo of Measurement |  | BCA | Code of Accessibility
15 | On the push side, a minimum space of 300 mm adjacent to the leading edge of the door with a minimum clear floor space of 1200 mm wide by 1200 mm deep. | >300mm | All Applicable Areas | Door | 1 | Photo of Measurement |  | BCA | Code of Accessibility
16 | The leading edge of the door leaf must not be set more than 150mm from the wall surface | <150mm | All Applicable Areas | Door | 1 | Photo of Measurement |  | BCA | Code of Accessibility
17 | Clear Width of Ramp | >1200mm | All Applicable Areas | Ramps | 1 | Photo of Measurement |  | BCA | Code of Accessibility
18 | Handrails that are placed at a height of between 800 mm and 900 mm above the floor level; and | >900mm x > 800mm | All Applicable Areas | Ramps | 1 | Photo of Measurement |  | BCA | Code of Accessibility
20 | Where service counters are provided, part of the counter shall not be more than 800 mm from the floor | <800mm | All Applicable Areas | Service and Information Counter | 1 | Photo of Measurement |  | BCA | Code of Accessibility
21 | An accessible gate with a width of 850 mm or more shall be provided beside a turnstile as shown in Figure 16. | >850mm | All Applicable Areas | Turnstile | 1 | Photo of Measurement |  | BCA | Code of Accessibility
22 | Areas with mode of ventilation indicated as AC or MV shall comply with SS 553. For AC systems, QP to confirm fresh air is provided to the system for ventilation of the room/space. | - | All Applicable Areas | Ventilation System | 1 for each type of system | Photo of Additional Evidence | To show picture of the MV outlet if it could not be seen from the Scan | BCA | Approved Document
26 | Headroom > 2.2m | >2200mm | Carpark | Common Parking Lots and Driveway | 3 | Photo of Measurement |  | BCA | Approved Document
27 | Safety barrier >1m | >1000mm | Carpark | Common Parking Lots and Driveway | 3 | Photo of Measurement |  | BCA | Approved Document
32 | The lift landing call button shall be located at least 350 mm away from a wall or obstruction | >350 mm | Lift | Lift Lobby for Accessiblity | 1 | Photo of Measurement |  | BCA | Code of Accessibility
33 | A momentary audible announcement must be provided to signal each call registered and the storey reached. | - | Lift | Lift Lobby for Accessiblity | 1 | Video Recording | To show for 1 accessible lift and the duration to be sufficient to hear the annoucements | BCA | Code of Accessibility
37 | Barrier's size of opening <500mm | <500mm | Maintenance Areas | Maintenance Areas | 3 | Photo of Measurement |  | BCA | Approved Document
39 | The width of the access route leading to the bathroom, or the room where the bathroom is, shall be a minimum of 1000 mm, subject to the provisions in Table 6. | >1000mm | Residential Unit | Accessible Route | 1 | Photo of Measurement |  | BCA | Code of Accessibility
40 | Difference in level between floor of the entrance to the residential unit and the abutting common area shall not be more than 50mm | <50mm | Residential Unit | Door | 1 | Photo of Measurement |  | BCA | Code of Accessibility |  |  | Yes
41 | The doorway of the bathroom for future retrofitting and the clear space in front of the doorway shall comply with the dimensions in Table 6 | - | Residential Unit | Retrofit Bathroom | 1 | Photo of Measurement |  | BCA | Code of Accessibility
42 | The bathroom for future retrofitting shall have a clear floor space of at least 1000 mm by 1000 mm at the front edge of the water closet. In addition, the WC shall be positioned by not less than 450mm from the wall. | >1000 by 1000 >450mm | Residential Unit | Retrofit Bathroom | 1 | Photo of Measurement |  | BCA | Code of Accessibility
43 | There shall preferably be no change in level of the floor surface at the doorway of the bathroom. If there is a change in level, it shall not be more than 25 mm. | <25mm | Residential Unit | Retrofit Bathroom | 1 | Photo of Measurement |  | BCA | Code of Accessibility |  |  | Yes
44 | A staircase shall have barriers against falling from 1.0m or more from an open side | >1000mm | Staircase Area | Barriers | 1 | Photo of Measurement |  | BCA | Approved Document
45 | The minimum clear width of staircase shall not be less than 1000mm. | >1000mm | Staircase Area | Staircase | 1 | Photo of Measurement |  | BCA | Approved Document
46 | The height of riser shall not be more than 175mm. | <175mm | Staircase Area | Staircase | 3 | Photo of Measurement |  | BCA | Approved Document
47 | Handrail height between 800mm and 1000mm | 1000mm > x > 800mm | Staircase Area | Staircase | 1 | Photo of Measurement |  | BCA | Approved Document
48 | Gap between handrail and wall, (>40mm for smooth finish, >60mm for rough finish) | >40mm (or >60mm) | Staircase Area | Staircase | 1 | Photo of Measurement |  | BCA | Approved Document |  |  | Yes
49 | The width of a tread of a staircase shall not be less than 225mm/250mm/275mm. | >225/250/275mm | Staircase Area | Staircase | 3 | Photo of Measurement |  | BCA | Approved Document
52 | Have minimum clear dimensions between opposite walls of 1750mm or more | >1750mm | Toilet area | Accessible Individual Washroom | 1 | Photo of Measurement |  | BCA | Code of Accessibility
53 | have a minimum clear floor space of 750 mm wide by 1200 mm deep from grab bars location and without steps in front of the urinals; and | >750mm by 1200mm | Toilet area | Ambulant Urinal | 1 | Photo of Measurement |  | BCA | Code of Accessibility
55 | grab bar inside the ambulant toilet shall be at least 600 mm long on the inside of an out-swinging door; | >600mm | Toilet area | Door | 1 | Photo of Measurement |  | BCA | Code of Accessibility
56 | grab bar located so that it is 130 mm or less from the hinged-side of the door; and | >130mm | Toilet area | Door | 1 | Photo of Measurement |  | BCA | Code of Accessibility
58 | be located between 460 mm to 480 mm from the centre line of the water closet to the adjacent wall and have a clear dimension of 750 mm from the front edge of the water closet to the rear wall to facilitate side transfer; | 480mm > x > 460mm | Toilet area | Water Closet | 1 | Photo of Measurement |  | BCA | Code of Accessibility
| Clearance of 2.0 m or more at the front of chiller unit piping section for tube maintenance and cleaning, repair and replacement of bigger components | ≥2000mm | Chiller plant area | Chillers | 1 | Photo of measurement |  | BCA | Code for Environmental Sustainability of Buildings, 4th edition
| Clearance of 1.2 m or more between the chillers measured from plinth to plinth for regular maintenance | ≥1200mm | Chiller plant area | Chillers | 1 | Photo of measurement | Both sides of one of the chillers | BCA | Code for Environmental Sustainability of Buildings, 4th edition
| Clearance of 1.5 m or more above the chiller to facilitate maintenance, overhaul or replacement | ≥1500mm | Chiller plant area | Chillers | 1 | Photo of measurement |  | BCA | Code for Environmental Sustainability of Buildings, 4th edition
| Except for the areas where the pipes are connected, clearance of 0.6 m or more is to be provided around the pump for regular maintenance | ≥600mm | Chiller plant and condenser area | Chilled water pumps and condensers water pumps | 1 | Photo of measurement | Front, back and sides of one of the chilled water and condenser water pumps | BCA | Code for Environmental Sustainability of Buildings, 4th edition
| Clear headroom of 1.0 m or more above the pump and motor to facilitate maintenance, overhaul or replacement. | ≥1000mm | Chiller plant and condenser area | Chilled water pumps and condensers water pumps | 1 | Photo of measurement |  | BCA | Code for Environmental Sustainability of Buildings, 4th edition
| Provision of maintenance platform, stairs and catwalks of 600 mm width or more with handrails around the cooling towers and access to the level for periodic maintenance and inspection of the water basin and fill media | ≥600mm | Cooling towers | Cooling towers | 1 | Photo of i) Overall view of cooling tower showing maintenance platform at fill media / louvres, ii) Measurement of maintenance platform width, iii) Handrails, iv) Access to cooling tower door, and v) Access to platform via staircase or cat ladder |  | BCA | Code for Environmental Sustainability of Buildings, 4th edition
| Clear distance of 2.0 m or more from the top of cooling towers to the location of the trellis, where applicable | ≥2000mm | Cooling towers | Cooling towers | 1 | Photo of measurement |  | BCA | Code for Environmental Sustainability of Buildings, 4th edition
| Air handling units (AHUs) of cooling capacity greater than 35 kW shall be floor mounted as stipulated in SS 553 | - | AHU area | AHU | All AHUs | Photo of AHU positioning (mounting type) and access to the AHU. |  | BCA | Code for Environmental Sustainability of Buildings, 4th edition
| Provide minimum 1.0 m clearance from the AHU room door entrance to the AHU for general maintenance | ≥1000mm | AHU area | AHU | 1 | Photo of measurement |  | BCA | Code for Environmental Sustainability of Buildings, 4th edition
| Provide minimum 800mm clearance after pipe connection to facilitate cooling coil cleaning and filter access | ≥800mm | AHU area | AHU | 1 | Photo of measurement |  | BCA | Code for Environmental Sustainability of Buildings, 4th edition
| Provide minimum 800 mm clearance for fan/motor access and maintenance (if the access is not from the cooling coil connection side) | ≥800mm | AHU area | AHU | 1 | Photo of measurement |  | BCA | Code for Environmental Sustainability of Buildings, 4th edition
| Provide minimum 600 mm clear width for general access and maintenance | ≥600mm | AHU area | AHU | 1 | Photo of measurement | Photo of clearance for sides of one of the AHUs other than those sides that comply with S/N 68 and 69. | BCA | Code for Environmental Sustainability of Buildings, 4th edition

## Dropdown (hidden)
Mode of Evidence | Type of Plan
Photo of Measurement | Typical
Photo of Additional Evidence | Non-Typical
Video Recording
Document Attachment