## Project Details
GMDC: 2024 for Existing Data Centres
Project Details |  |  |  |  | Possible inputs
GM Reference No
Building Name
Address
Type of Building | Existing Data Centres |  |  |  | Office / Retail / Hotel / Mixed Office + Retail
Type of Data Centre | Enterprise / Co-locator
GFA (m2)
Carpark Area (m2)
Air-conditioned Area (m2)
Building Key Performance Data:
Type of Aircon system |  |  |  |  | Central Water-cooled Chiller Plant / VRF System / Unitary System
| 100% IT Load | 75% IT Load | 50% IT Load | 25% IT Load
IT load capacity (MW)
PUE (kWh/kWh)
Building cooling load (RT)
Chiller configuration (e.g. 3 nos. x 500RT)
Air Distribution system efficiency (kW/RT)
Total System Efficiency, TSE (kW/RT)
Total Building Energy consumption (kWh/yr)
EUI (kWh/m2/yr)
Reason for Certification

## Summary
GMDC: 2024 ScoreCard for Existing Data Centres
GM Ref No. | 0
Project Name: | 0
Revision:
SUMMARY
| MAX POINTS | SCORING POINTS | REMARKS
Energy Efficiency | 40 | #VALUE!
Carbon | 8 | 0
Resilience | 6 | 0
Health and Wellbeing | 3 | 0
Intelligence | 9 | 0
Maintenance | 9 | 0
TOTAL | 75 | #VALUE!

## 1. Energy Efficiency
CRITERIA FOR ENERGY EFFICIENCY SECTION |  | Data Input | Input Required | Available points for Existing Buildings | Points Scored | Remarks | Working
ENERGY EFFICIENCY |  |  |  | 40 | #VALUE! | -
| Building supplied by District Cooling System? |  | Y/N
EE 1 | Power Usae Effectiveness (PUE)
(a) | New Data Centres | N.A. | [8 empty] | 25% | 50% | 75% | 100% | 0% | 25-50 | 50--75 | 75-100
(b) | Existing Data Centres - Operating PUE |  | Input (#) | 20 | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | Gold+ | 1.46 | 1.39 | 1.36 | 1.35 | error | 1.53 | 1.45 | 1.39
| - Operating IT Load |  | Input (%) | [6 empty] | Platinum | 1.39 | 1.32 | 1.29 | 1.28 | error | 1.46 | 1.38 | 1.32
| SUB-TOTAL FOR EE 1 |  |  |  | #VALUE!
EE 2 | Cooling System Efficiency
| Total System Efficiency |  | Input (#) | 10 | 0 |  | 27.42
| Air-Side Efficiency (For DCS) |  | Input (#) | 10 | 0 |  | 21
| SUB-TOTAL FOR EE 2 |  |  |  | 0
EE 3 | Air Management
(a) | Using CFD simulation to analyse and improve air management | N.A.
(b) | Existing Data Centres Return Temperature |  | Input (%) | 1.5 | 0
| (i) Range between 70% and 130% | [5 empty] | (i) Range between 70% and 130% | 0.5
| (ii) Range between 80% and 120% | [5 empty] | (ii) Range between 80% and 120% | 1
| (iii) Range between 90% and 110% | [5 empty] | (iii) Range between 90% and 110% | 1.5
(c) | Supply Air Temperature (SAT) of air leaving aircon unit |  | Input (#) oC | 1.5 | 0
| SUB-TOTAL FOR EE 3 |  |  |  | 0
EE 4 | IT Power Chain Efficiency
| IT power chain efficiency ≥85% at operating IT load |  | Input (%) | 4 | 0 |  | -24.5
| SUB-TOTAL FOR EE 4 |  |  |  | 0
EE 5 | Hot Aisle / Cold Aisle Containment
| Implemented Hot Aisle / Cold Aisle Containment |  | Y/N | 2 | 0
| SUB-TOTAL FOR EE 5 |  |  |  | 0
EE 6 | Renewable Energy
| To promote on-site renewable energy generation in order to reduce reliance on grid energy and decrease carbon emissions. |  | Input (%) | 1 | 0 |  | 0
| SUB-TOTAL FOR EE 6 |  |  |  | 0

## 2. Carbon
| CRITERIA FOR CARBON SECTION |  |  | Data Input | Input Required | Available points for Existing Buildings | Points Scored | Remarks
Carbon | [5 empty] | 8 | 0 | -
CN1 | Sustainable Design and Construction |  |  | N.A.
(a) | Scalable expansion by building up capacity in a modular approach
(b) | Use of Low Carbon Concrete certified by SGBC or equivalent local certification bodies (using CEM II – V cements under SS EN 197-1) for ≥80% of applicable superstructure works by volume
SGBP 2 ticks/ SGBP 3 ticks/SGBP 4 ticks or equivalent administered by local certification bodies
(c) | Replacement of aggregates Replacement of coarse and fine aggregates for structural concrete applications [by mass of Crushed Concrete Aggregates (CCA), Washed Copper Slag (WCS), granite fines (GF)] must meet both minimum requirements in terms of extent of usage and replacement levels
Total concrete use for superstructure (m3)
Replacement level of coarse aggregate with CCA ≥ 20%
Minimum extent of usage of CCA ≥ 1.5% of GFA
Replacement level of fine aggregate with WCS used for superstructure ≥ 10%
Minimum extent of usage of WCS ≥ 0.75% of GFA
Replacement level of fine aggregate with GF used for superstructure ≥ 50%
Minimum extent of usage of GF ≥ 1.5% of GFA
(d) | Existing structures are demolished with an enhanced demolition protocol, where a recovery rate of ≥ 40% of crushed concrete waste from demolished building sent to approved recyclers with proper recycling facilities
| SUB-TOTAL FOR CN1 | [5 empty] | 0
CN2 | Sustainable products and materials
(a) | ≥ 60% (by cost) of Mechanical, Electrical and Plumbing (MEP) systems are SGBP certified (or equivalent) administered by local certification bodies At least 3 MEP systems |  |  |  | Input (%) | 0.5 | 0 | (to list the 3 systems here)
(b) | Green Materials Points awarded based on weightage and the extent of the coverage and impact (i.e. weightage x extent of coverage and impact) |  |  |  | Weightage | 0.5 | 0 |  | Column1 | Column2 | Column1 | Column2 | 0 | 0
[5 empty] | Extent of Coverage |  |  |  | Very Good | 0.3 | High Impact | 0.5
[5 empty] | Weightage |  | 0 |  | Excellent | 0.4 | Low Impact | 0.25 | 0 | 0
| Very Good | Excellent | Leader |  | Extent of Coverage |  |  |  | Leader | 0.5
| 0.3 | 0.4 | 0.5 |  | Weightage |  | 0 | [5 empty] | 0 | 0
Extent of Coverage
| Factor Based on Extent of Coverage and Impact of the Material |  |  |  | Weightage |  | 0 | [5 empty] | 0 | 0
Extent of Coverage
| High Impact | 0.5 |  |  | Weightage |  | 0 | [5 empty] | 0 | 0
| Low Impact | 0.25 |  |  | Extent of Coverage
[5 empty] | Weightage |  | 0 | [5 empty] | 0 | 0
| Note: High impact refers to ≥60% of usage; Low impact refers to <60% usage of applicable areas |  |  |  | Extent of Coverage
[5 empty] | Weightage |  | 0 | [5 empty] | 0 | 0
Extent of Coverage
| SUB-TOTAL FOR CN2 | [5 empty] | 0
CN3 | Energy Efficient IT Equipment
| IT equipment must have a valid certificate under US Energy Star or equivalent certification scheme. In cases where Energy Star or equivalent certification is not available, individual compute server equipment’s active state efficiency score obtained using Standard Performance Evaluation Corporation (SPEC)’s Server Efficiency Rating Tool (SERT) ver. 2.0 and above shall be provided to show that the equipment is as energy efficient as that specified by Energy Star or equivalent certification. |  |  |  | Input (%) | 3 | 0
IT equipment shall be able to operate at Class A2 conditions as defined by ASHRAE Environment Classes for Data Centres.
| Coverage of IT equipment <50% | 0 | point
| 50% ≤ Coverage of IT equipment < 70% | 1 | point
| 70% ≤ Coverage of IT equipment < 85% | 2 | points
| Coverage of IT equipment ≥ 85% | 3 | points
Note: Coverage of IT equipment refers to the percentage of the total number of IT equipment or the total rated power of the IT equipment in a DC that meets the above criteria
| SUB-TOTAL FOR CN3 | [5 empty] | 0
CN4 | SS 564 Certification
| To obtain SS 564 certification which assists organizations in establishing and maintaining a management system focused on energy efficiency and environmental stewardship |  |  |  | Y/N | 2 | 0
| SUB-TOTAL FOR CN4 | [5 empty] | 0
CN5 | Greenhouse Gas (GHG) Emissions Monitoring and Tracking
(a) | Scope 1 GHG emission (direct emission) and Scope 2 GHG emission (indirect emission) |  |  |  | Y/N | 1 | 0
(b) | Scope 3 GHG emission (indirect emission) for at least 2 relevant categories |  |  |  | Y/N | 1 | 0
| SUB-TOTAL FOR CN4 | [5 empty] | 0

## 3. Resilience
| CRITERIA FOR RESILIENCE SECTION | Data Input | Input Required | Available points for Existing Buildings | Points Scored | Remarks
Resilience |  |  |  | 6 | 0 | -
RE1 | Project Team
(i) | Appointment of accredited environmentalist specialists to drive and coordinate the environmental design approach. | [6 empty] | Sub-total
| Certified GM AP / GM AP(FM) |  | Y/N | 0.25 pts/GMAP/CFME & 0.5 pts /GM AAP (Capped at 0.5 pts) | 0 |  | 0 | 0 | Max 0.5 pt
| Certified GM AAP / GM AAP(FM) |  | Y/N |  |  |  | 0
| Certified FM Expert (CFME) - Tiers 1 and 2 |  | Y/N |  |  |  | 0
(ii) | No. of firms certified under SGBC's SGBS certification or SIFMA's CFMC accreditation scheme. |  | Input (#) | 0.25 pts/firm (Capped at 0.5 pts) | 0 | List the firm(s) | 0 | 0 | Max 0.5 pt
| SUB-TOTAL FOR RE1 |  |  |  | 0
RE2 | Refrigerant and Fire Suppressant
Points will be awarded based on the Ozone Depleting Potential (ODP) and Global Warming Potential (GWP) for the following (ODP=0 and GWP<10):
(a) | Refrigerants |  | Y/N | 1 | 0
(b) | Fire Suppressant in the whole data centre |  | Y/N | 1 | 0
Note: To be awarded any points, all refrigerants and fire suppressants used throughout the data centre must comply with these criteria.
| SUB-TOTAL FOR RE2 |  |  |  | 0
RE3 | Reduction in Water Consumption of Cooling Towers | [6 empty] | Column1 | Column2
(a) | Use of a cooling tower water treatment system which can achieve - 7 or better cycles of concentration (COC) with acceptable water quality when utilising PW ; OR - 10 or better cycles of concentration (COC) with acceptable water quality when utilising NW |  | Y/N | 0.5 | 0 |  |  | N.A. | 0
(b) | Use of alternate water for cooling tower makeup water such as rainwater, AHU condensate water, NEWater, etc. |  | Y/N | 0.5 | 0 | State alternate water source |  | COC≥ 7 with PW | 0.5
| Note: DCs are to provide cooling tower water conductivity sensors for real-time COC trending and monitoring. | [6 empty] | COC≥10 with NW | 0.5
| SUB-TOTAL FOR RE3 |  |  |  | 0
RE4 | Water Efficient Fittings
| Use of minimum WELS 3-ticks rating for all water fittings |  | Y/N | 1 | 0
| SUB-TOTAL FOR RE4 |  |  |  | 0
RE5 | Water Usage Effectiveness (WUE)
| Points will be awarded for WUE less than 2.2m3/MWh/year. WUE (m³/MWh/year) = Annual Water Consumption (m3) / Annual IT energy (MWh) |  | Input (#) | 1 | 0
| SUB-TOTAL FOR RE5 |  |  |  | 0

## 4. Health and Wellbeing
| CRITERIA FOR HEALTH & WELLBEING SECTION | Data Input | Input Required | Available points for Existing Buildings | Points Scored | Remarks
Health & Wellbeing |  |  |  | 3 | 0 | -
HW1 | Active Furnishing |  |  | 0.5
| Active Furnishing Provision of active furnishing to discourage sedentary behaviour (e.g. standing tables and height-adjustable desk), decentralised common areas, standing meeting rooms etc. (at least 100% of all workstations) |  | Y/N | 0.5 | 0
Sub-Total for HW1 |  |  |  |  | 0
HW2 | Air Quality and Comfort
(a) | Occupant Comfort
(i) | Use of hybrid cooling system (elevated temperature with increased air speed) that can meet PMV +/- 0.5 |  | Y/N | 0.25 | 0
(ii) | Periodic (Post) Occupancy Evaluation At least once every 3 years |  | Y/N | 0.25 | 0
(iii) | IAQ Surveillance Audit By an accredited laboratory once very 3 years |  | Y/N | 0.25 | 0
(b) | Clean Air
(i) | UVGI system for air disinfection |  | Y/N | 0.25 | 0
(ii) | Air Filtration Permanent provision of ePM1 ≥75% (ISO 16890) [or alternatively at least MERV 14A (ASHRAE 52.2 Appendix J)] media filters for occupied space |  | Y/N | 0.25 | 0
Sub-Total for HW2 |  |  |  |  | 0
HW3 | Biophilic Design
Direct connection to plants, water, light or nature views; Indirect connection via natural materials, patterns, art; Placement of natural elements along common circulation routes, shared seating areas, workstations
(i) | Fixed indoor planting distributed at key common areas. >10% of common area (by floor Area) to have fixed indoor planting, and/or ponds. |  | Y/N | 0.5 | 0
(ii) | Placement of natural elements, and use of mixed textures in key common areas such as atria, entrance lobbies, shared seating areas, and key circulation routes. |  | Y/N | 0.5 | 0
Sub-Total for HW3 |  |  |  |  | 0
HW4 | Restorative Spaces |  |  | 5
| Designated indoor and/or outdoor space for restorative practices (minimum 16m2 per space, and large enough for meditation/yoga or just quiet respite) which are accessible for all building occupants. |  | Y/N | 0.25 | 0
Sub-Total for HW4 |  |  |  |  | 0

## 5. Intelligence
| CRITERIA FOR INTELLIGENCE SECTION | Data Input | Input Required | Available points for Existing Buildings | Points Scored | Remarks
Intelligence |  |  |  | 9 | 0 | -
IN1 | Integration
(a) | Digital Life Cycle
(i) | PIM (BIM) developed in accordance with Singapore Model Content Requirements (MCR).
(ii) | Use of spatial model co-ordination platform based on PIM for spatial analysis including:
a. Identifying system clashes through an automatic model checking tool
b. Spatial analysis for effective construction, maintenance and future alteration or replacement.
(iii) | Digital building commissioning, performance and defect co-ordination platform based on PIM to track, co-ordinate and manage the commissioning of systems and the tracking of defects and their rectification. |  | Y/N | 1 | 0
(b) | Performance dashboard
Performance dashboard to monitor the different aspect of building assets’ performance and operations from a single dashboard:
| i. Operational dashboard: sets of measures used to guide facility operations such as energy & water efficiency and work order status. |  | Y/N | 1 | 0
| ii. Managerial dashboard: sets of metrics which may use data from multiple operational systems such as asset health and energy use per occupant. |  | Y/N | 1 | 0
(c) | Data Accessibility and Security
| Iinformation stored in the digital platform(s) can be accessed by facilities teams in a secured manner to facilitate operation and maintenance activities from anywhere and anytime. |  | Y/N | 0.5 | 0
| SUB-TOTAL FOR IN1 |  |  |  | 0
IN2 | Asset Information Model
(a) | Physical and virtual asset information tagging system that allows for tracking of maintenance work, repairs, refurbishments or upgrades, replacement, decommissioning, risk assessments, and performance evaluations of the physical asset to be captured. |  | Y/N | 1 | 0
(b) | Demonstrate accountable data ethics practices that identifies the various opportunities for the collection, analysis, and use of data, organised around 4 principles: a) Governance and Transparency b) Management of Personal Data c) Care of Personal Data d) Individuals’ Rights |  | Y/N | 1 | 0
| SUB-TOTAL FOR IN2 |  |  |  | 0
IN3 | Responsive
(i) | Adaptive ACMV control system (Water Side) – continuously monitor, analyse, and modify BMS control settings to optimise energy usage of ACMV (water-side) system |  | Y/N | 1 | 0
(ii) | Adaptive ACMV control system (Air Side) – continuously monitor, analyse, and modify BMS control settings to optimise energy usage of ACMV (air side) system |  | Y/N | 1 | 0
(iii) | Adaptive lighting monitoring & control system – continuously monitor and control the lighting within specific areas based on inputs such as motion, daylight levels, or space temperature to reduce energy usage |  | Y/N | 0.5 | 0
(iv) | Tenant energy monitoring and optimisation – continuously monitor, benchmark, and report tenant energy consumption to optimise the energy consumption. |  | Y/N | 1 | 0
| SUB-TOTAL FOR IN3 |  |  |  | 0

## 6. Maintainability
| CRITERIA FOR MAINTAINABILITY SECTION | Data Input | Input Required | Available points for Existing Buildings | Points Scored | Remarks | Points Scored from Embedded Scoresheet | Points Scored from Embedded Scoresheet
Maintainability |  |  |  | 9 | 0
MT1 | Architectural |  |  |  |  | - | 0 | 0
| Ensure entire façade is accessible for maintenance |  | Y/N | 1 | 0 |  | 0 | 0
| SUB-TOTAL FOR MT1 |  |  |  | 0 |  | 0 | 0
MT2 | Mechanical |  |  |  |  | - | 0 | 0
2.1 | Chiller Plant | [5 empty] | 0 | 0
2.1.1 | Access to cooling towers to facilitate maintenance Provide permanent sleeve to mount davit arm for all cooling towers and hand over of 1 davit arm for each cooling tower model to building owner. |  | Y/N | 0.5 | 0 |  | 0 | 0
2.1.2 | Reduce risk of fouling issue and improve condenser water quality
(a) | Provide microprocessor based, automatic water quality monitoring and control system linked to BMS. The critical parameters including conductivity, temperature, pH value, hardness, salinity, oxidation reduction potential (ORP) and total dissolved solids (TSS) must be monitored by BMS. |  | Y/N | 0.5 | 0
(b) | Provide auto-tube cleaning for water cooled chillers. |  | Y/N | 0.5 | 0
(c) | Provide basin sweeper system and side stream separator to remove coarse to fine particles and silt deposit in the cooling tower basin. Note: The basin sweeper system shall be provided for each cooling tower. |  | Y/N | 1 | 0
2.2 | Fire Protection System | [5 empty] | 0 | 0
2.2.1 | Provide flexibility for maintenance and testing of sprinkler system
(a) | Locate the flow switch drain valve in rooms with floor trap (i.e. toilet, AHU room etc.). |  | Y/N | 0.5 | 0
(b) | Provide smart features such as the automatic flow switch testing system to automate the functional test for the fire sprinkler system. |  | Y/N | 0.5 | 0
2.2.2 | Reduce risk of damage and periodic replacement of fire-rated boards due to exposure to high humidity and water.
(a) | Specify the use of weatherproof fire-rated materials for fire protection services such as wet/dry riser and hydrant pipes etc. |  | Y/N | 0.5 | 0
(b) | Specify the use of weatherproof fire-rated materials for mechanical ventilation services. |  | Y/N | 0.5 | 0
| SUB-TOTAL FOR MT2 |  |  |  | 0 |  | 0 | 0
MT3 | Electrical |  |  |  |  | - | 0 | 0
3.1 | Power Distribution | [5 empty] | 0 | 0
3.1.1 | Reduce risk of water Ingress into electrical room
(a) | Electrical room must be raised by min 100 mm against the outside passageway. |  | Y/N | 0.5 | 0
(b) | Provide min 100 mm plinth for floor mounted electrical switchboard.
3.1.2 | Reduce risk of failure of main LT switchboard due to overheating | [5 empty] | 0 | 0
(a) | Install heat sensor in the main LT switchboard to alert any abnormal rise in temperature with audible/visual alarm. |  | Y/N | 0.5 | 0 |  | 0 | 0
(b) | Integrate sensor to building BMS system for online monitoring of temperature data. |  | Y/N | 0.5 | 0 |  | 0 | 0
3.2 | Lighting Protection System
| Reduce risk of damage of air termination tape at roof parapet wall due to operation of façade maintenance systems such as gondola Avoid damage to the lightning protection system by proper design and installation of facade maintenance system |  | Y/N | 0.5 | 0
3.3 | Vertical Transportation
(a) | Provide access to roof level for equipment replacement and maintenance such as chiller plant and pumps |  | Y/N | 0.5 | 0
(b) | Reduce lift downtime and enhance reliability by providing lift predictive maintenance. |  | Y/N | 0.5 | 0
Note: Monitor key parameters such as vibration, acceleration, levelling, door jams, gaps, noise, and jerk etc.
3.4 | CCTV Camera
(a) | Provide access to cameras located at heights (≥3 m) i.e. foldable poles/arms |  | Y/N | 0.25 | 0
(b) | Provide surge arrestor to all outdoor cameras |  | Y/N | 0.25 | 0
| SUB-TOTAL FOR MT3 |  |  |  | 0