## Temperature Sensors
Temperature Sensors Check
Purpose: | For checking the accuracy of temperature sensors used in chiller plant system with help of portable accurate temperature sensors and spare thermowells
Estimated time to fill up the excel: | 1 hour | (assume 6 mins for each of the 4 easy-to-access temperature measurements with no rework. Time spent will be longer with longer logging interval, more measurements required and more challenging thermowell locations.)
Steps: | 1. Ensure temperature sensors onsite are as calibrated with matching serial numbers in corresponding calibration certificates. The portable accurate temperature sensor to be used is calibrated within a year, accurate up to 0.01°C 2. Check and ensure that each temperature sensor coefficients (eg a,b and c are coefficients obtainable from the calibration certificate) are keyed in correctly in the BMS. 3. Set up the BMS data trending to be the same or as an interval divisor for subsequent data logger polling rate (of the portable accurate temperature sensor) such as 1 min, 10s or 5s interval. This set up is recommended only during the temperature sensor site measurement. The team can adjust the BMS trending later back to normal interval. 4. Synchronise the timing between the measurement device and BMS to be the same. 5. Set data logger polling rate to be the correct interval. Conduct temperature measurement for at least 30 samples for each measurement point. This could include using a test probe to make sure that the spare thermowell is able to allow the sensor to be inserted before conducting the measurement. 6. Extract BMS data during temperature measurement. 7. Compare the readings between the temperature sensor measurement and BMS readings using the same time stamp, including plotting of graphs. 8. Take the average of absolute difference of the readings for at least 30 samples using the excel. It shall not exceed 0.07 °C. 9. Shift the plotted graphs if lead or lag. 10. These temperature sensor measurements are only applicable for those permanent temperature sensors which are being used for calculating the system efficiency and heat balance. Please create more calculations if there are more measurement points being used ( eg of the typical permanent temperature sensors are at – CHWS, CHWR, CWS, CWR headers).
* Please make reference to PEA code (3.00 Edition) Appendix B Worked Example
PEA Code (3.00 Edition)
Project Name :
GM ref no :
Date of testing :
Submitted by : |  |  |  | Company :
I declare that the information submitted are done based on accepted methodologies and all information are as per recorded and measured. There is no alteration, tempering whatsoever to the data to meet requirements. Declaration is not required for PEA submission where it is assumed.
Witness by : |  |  |  | Company :
Calibration ref no: |  |  |  | Date of equipment’s calibration:
CHWS Temperature (°C) |  |  |  | CHWR Temperature (°C)
Time | Consultant | BMS | ABS Diff | Time | Consultant | BMS | ABS Diff
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  | Average | 0 |  |  | Average | 0
CDWS Temperature (°C) |  |  |  | CDWR Temperature (°C)
Time | Consultant | BMS | ABS Diff | Time | Consultant | BMS | ABS Diff
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  |  | 0 |  |  |  | 0
|  | Average | 0 |  |  | Average | 0