## Project Detail
GMDC: 2024 In Operation is applicable for existing Data Centres which have perviously attained Green Mark Certification, are applying for recertification, and have not done any major retgrofit*.
GMDC: 2024 In Operation
Projects Details:
GM Reference No.
Project Name
Gross Floor Area (m2)
Previous GM Reference No.
Previous GM rating
Data Centre Key Performance Data:
Data Centre Type
Data Centre Age
Type of Air-conditioning System
Operating Total System Efficiency (kW/RT)
IT load Capacity (Total) (MW)
Current IT load (MW
Operating PUE
*Major retrofit - pls refer to the definition in GM: 2021

## Criteria
1. Operating PUE
PUE is a metric that illustrates data centre energy efficiency using the total annual facility energy divided by total annual IT equipment energy. The IT equipment energy shall be measured at Power Distribution Unit (PDU) output [PUE category 2]. Please refer to SS 564 for details on the PUE metric and the measurement categories. PUE performance data for past 12 months shall be submitted.
2. Operating TSE
| Green Mark Rating | Gold | GoldPLUS | Platinum
| Total Cooling System Efficiency (TSE) (kW/RT) | 0.8 | 0.74 | 0.68
| Airside Efficiency (kW/RT) (Applicable only for DCs with purchased cooling from District Cooling System (DCS) | 0.2 | 0.18 | 0.16
i) Total Cooling System Efficiency (TSE) (kW/RT) shall include both the water side and air side systems, irrespective of types of cooling systems and IT loads.
ii) Air-side Efficiency (kW/RT) is required for DCs with purchased cooling from District Cooling System (DCS), irrespective of types of cooling systems and IT loads.
3. IT Power Chain Efficiency
IT Power Chain Efficiency shall be at least 85% and include components such as transformers, transmission lines, switchgears, UPSs and PDUs serving the IT equipment.
4. Water Efficiency
a. Water Usage Effectiveness (WUE)
WUE is a metric that measures the efficiency of water usage in data centres. To encourage water use efficiency in data centres.
b. Cycle of Concentration of Cooling Tower
Use of a cooling tower water treatment system which can achieve 7 or better cycles of concentration (COC) with acceptable water quality when utilising PW, or 10 or better cycles of concentration (COC) with acceptable water quality when utilising NW
5. Energy and Water Improvement Plans
To establish sustainability targets, implementation measures and improvement plans to achieve the target set over the next three years:
a. Energy improvement plan
b. Water improvement plan
6. IAQ Surveillance Audit and Post Occupancy Evaluations (POE)
a. To Conduct IAQ Surveillance Audit on occupied areas once every 3 years. The audit shall be conducted by an accredited laboratory under Singapore Accreditation Council
b. To conduct a POE survey on occupied areas once every 3 years and take corrective actions accordingly.

## Operating PUE
Operating PUE
| year 1 | year 2 | year 3 | Remark
PUE
% IT Load
Total Energy consumption (kWh) [A]
Total IT Energy (kWh)
EUI (kWh/m2 of GFA) = [A]/GFA
PV Generation (kWh)

## Operating TSE
Operating TSE
Summary of OSE report for TSE | Pls attach OSE report here
Daily Average Reading | Results (24 hrs) | Unit
Cooling Load |  | RT
Cooling Load Density (by aircon area) |  | m²/RT
Energy Consumption from Chilled water side (chillers/pumps/CT) |  | kW
Chilled water supply temperature |  | °C
Chilled water return temperature |  | °C
Chilled water delta T |  | °C
Chilled water flow rate |  | l/s
Chilled water flow rate vs cooling load |  | USGPM/RT
*Condenser heat rejection |  | HRT
*Condenser water supply temperature |  | °C
*Condenser water return temperature |  | °C
*Condenser water delta T |  | °C
*Condenser water flow rate |  | l/s
*Condenser water flow rate vs cooling load |  | USGPM/RT
Chiller(s) efficiency |  | kW/RT
Chilled water pump(s) efficiency |  | kW/RT
*Condenser water pump(s) efficiency |  | kW/RT
*Cooling tower(s) efficiency |  | kW/RT
Energy consumption from airside |  | kW
Airside distribution system efficiency |  | kW/RT
Total System Efficiency (TSE) |  | kW/RT
* Not applicable to air-cooled chilled water plant
Summary of Heat Balance
| Data | Unit | Formula
Sum of total electrical energy used |  | kWh | A
Sum of total cooling produced |  | Rth | B
Sum of total heat rejected |  | Rth | C
Chiller platn efficiency |  | kW/RT | A/B
Total Heat Balance Data Count |  | - | D
Data Count > +5% error |  | - | E
Data Count < -5% error |  | - | F
Data Count within 5% error |  | - | G=D-E-F
% Heat Balance within 5% error |  | % | 100 x G/D

## IT Power Chain Efficiency
IT Power Chain Efficiency
IT Power Chiain Efficiency: | %
Single line diagrame showing the upstream meters and downstream meters used to calculate the IT power chain efficiency |  | Pls attach the electrical single line diagram here
Assessor's comment:
Excel calculation showing the calculation of IT power chain efficiency |  | Pls attach the detail calculation here
Assessor's comment:

## Water Efficiency
Water Efficiency
a. Water Uusage Effectiveness | WUE | Pls attache the calculation of WUE using past 12 months data here
Assessor's comment:
b. Cycle of Concentration | Cycles | Pls attach lastest past 3 months water treatment report here
Assessor's comment:

## Improvement plans
Energy and Water Improvement Plans
Submission of plans showing intent, measures and implementation strategies to achieve improvement target set against current performance over the next 3 years.
a. 3 years energy improvement target | % | Pls attache the energy improvement plan here
Assessor's comment:
b. 3 year water improvement target | % | Pls attache the water improvement plan here
Assessor's comment:

## IAQ and POE
IAQ and POE
a. IAQ Audit | Pls attach IAQ audit report here
Submission of latest IAQ audit report performed by SAC accredited lab/company, stating major areas of
Test Report number:
Date of audit conducted:
Name of SAC lab/company:
Assessor's comment:
b: POE survey | Pls attach POE survey here
Submit latest POE survey results (at least 10% occupancy)
Assessor's comment: